- GENERAL

  - DESCRIPTION

    - Section Includes

      - Sensors, cables, and associated equipment for measuring ammonium in water and wastewater treatment systems.  Controllers and modules required for a complete monitoring system are specified elsewhere.

    - Scope

      - Furnish, install, calibrate, test, adjust, and place into satisfactory operation ammonium measurement systems as shown on the Drawings and specified herein.

      - The Drawings and Specifications illustrate and specify functional and general construction requirements of ammonium measurement systems and do not necessarily show or specify all components, wiring, piping, and accessories required to make a completely integrated system. Provide all components, piping, wiring, accessories, and labor required for a complete and integrated system.

    - Coordination:  Coordinate with other suppliers for installation of all items specified herein and required to ensure the complete and proper interfacing of all the components and systems.

  - PERFORMANCE REQUIREMENTS

    - Design Requirements

      - Design ammonium measurement system for continuous monitoring in situ.

      - Ammonium measurement system shall be a component of a process monitoring system capable of monitoring up to 20 parameters simultaneously on each controller.  Measurement locations shall be networked together in a linear, star, or branched topology with a single 2-wire cable that distributes 12 V power and communications.

Note to specifier:  Item 1.2.A.2 is for a System 2020XT monitoring system.

      - The ammonium sensor assembly shall be a separate unit from the sensor connection cable and able to be located anywhere in the monitoring network a SensorNet terminal is available.

    - Performance Requirements

      - Operating range:

        - Temperature:  32°F to 104°F (0°C to 40°C).

        - Maximum overpressure:  0.2 bar

        - pH:  4 S.U. to 8.5 S.U.

      - Measuring range:

        - Ammonium as N:  0.1 mg NH4-N / L to 2,000 mg NH4-N / L

        - Potassium as K:  0.1 mg K+ / L to 1,000 mg K+ / L.

        - Temperature:  32°F to 104°F (0°C to 40°C).

        - Voltage:  -2,000 mV to 2,000 mV.

      - Measuring accuracy:

        - Ammonium, in standard solutions:  ± 5% of measured value or 0.2 mg/L.

        - Temperature:  ± 0.5K

      - Resolution:

        - Ammonium as N:  0.1 mg NH4-N / L.

          - 0.1 mg NH4-N / l to 100.0 mg NH4-N / L:  0.1 mg NH4-N / L.

          - 1 mg NH4-N / l to 2,000 mg NH4-N / L:  1 mg NH4-N / L.

        - Potassium as K:

          - 0.1 mg K / l to 100.0 mg K / L:  0.1 mg K / L.

          - 1 mg K / l to 1,000 mg NH4-N / L:  1 mg K / L.

        - Temperature:  0.1 °C.

        - Voltage:  1 mV

      - Response Time:

        - Ammonium:  90 percent of the final (true) reading in less than 180 seconds at a temperature of 20°C for a concentration change of 10 mg NH4-N / l to 100 mg NH4-N / l.

        - Potassium:  90 percent of the final (true) reading in less than 180 seconds at a temperature of 20°C for a concentration change of 5 mg K / l to 50 mg K / l.

        - Temperature:  95 percent of the final (true) reading in less than 20 seconds.

    - Compensation:  Compensation for to 1,000 mg K / l shall be automatic and dynamic with optional K electrode.

  - QUALITY ASSURANCE

    - Acceptable Manufacturers:

      - Furnish Ammonium sensors by the named manufacturers.

      - The named manufacturers have been specified to establish the standard of quality and performance of the equipment to be supplied.

      - Manufacturer shall be ISO 9001 certified.

  - PRODUCT DELIVERY, STORAGE, AND HANDLING

    - Ammonium measurement system shall not be delivered to the site until all product information and system shop drawings for the system have been approved.

    - Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

    - Storage and Handling Requirements:

      - Store and handle materials in accordance with manufacturer’s instructions.

      - Keep materials in manufacturer’s original, unopened containers and packaging until installation.

      - Store materials in clean, dry area indoors.

      - Protect materials during storage, handling, and installation to prevent damage.

      - Temperature range for storage:  32°F to 149°F (0°C to 65°C)

  - SUBMITTALS

    - Product data

      - Sensor operating manual.

      - Mounting bracket / sensor holder installation instructions.

    - Manufacturer’s Certifications:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

    - Warranty documentation:  Submit manufacturer’s standard warranties.

- PRODUCTS

  - GENERAL

    - Measurement principle shall be potentiometry by means of an ion selective electrode.

    - Connect ammonium sensor assembly to field-mounted junction box or expansion modules specified in Section 40 95 00 with sensor connecting cable specified in Section 2.3.A.3.

    - Ammonium measurement system components shall be designed to be part of an analytical process control system with enhanced protection from overvoltage due to lightning and power supply fluctuations according to EN 61326 when installed using manufacturer’s recommended components per manufacturer’s instructions.

  - MANUFACTURER

    - Provide products from the following manufacturer:

      - YSI Incorporated, 1700/1725 Brannum Lane, Yellow Springs, OH  45387

  - MANUFACTURED UNIT

    - The ammonium measurement system consists of the following:

      - Electrodes

        - Model VARiON®Plus NH4 electrode.

        - Model VARiON® Ref reference electrode.

        - Model VARiON®Plus K electrode. [Optional for most accurate measurements]

      - Model AmmoLyt® Plus 700IQ sensor assembly:

        - Integrated NTC thermistor.

        - Pre-amplification of electrode signal.

        - Digital signal processing with calibration value storage.

        - The sensor shall detach from sensor cable allowing for easy replacement or repair.

Note to specifier:  AmmoLyt® Plus 700IQ sensor assemblies can also be specified in sets that include the ammonium electrode, reference electrode, and optional compensation electrode.  Consult YSI for more information.

      - SACIQ-x,x [SACIQ-x,x SW] sensor connection cable.

        - Capable of transmitting digital communications and low voltage (24V) power

        - Integrated shield.

        - Connections

          - Sensor-side:  Quick fastener (threaded).

          - Controller-side:  tinned conductors

Note to specifier:  Specify appropriate length of cable in meters, e.g. SACIQ-1,5 is 1.5 m.   Standard lengths are 1.5 m, 7m, and 15m.  Custom lengths up to 100 m are available.  Select SACIQ-x,x for measurements in water/wastewater applications.  Select SACIQ-x,x SW for measurements in seawater/aquaculture and other highly corrosive environments.

  - MATERIALS

    - Electrodes

      - Ammonium and Potassium electrodes

        - Enclosure:  POM.

        - Clamping ring:  POM.

        - Membrane:  soft PVC with stainless steel protective grating.

        - Sealing ring:  Viton®.

        - Connection contacts:  gold plated.

        - Warranty:  1 year

      - Reference electrode

        - Enclosure:  PVC.

        - Junction:  Porous PVDF.

        - Sealing ring:  Viton®.

        - Connection contacts:  gold plated.

    - Sensor assembly

      - Shaft:  V4A stainless steel.

      - Protective hood:  POM

      - Fixing Ring:  POM

      - Protection cap:  PVC

      - EMI/RFI conformance

        - EN 61326 Class B

        - FCC Class A

      - Safety

        - Certification: CE,  cETLus

      - Protection rating:  IP68

      - Warranty: 2 yrs.

    - Sensor connection cable

      - Conductors:  Tin-coated stranded copper wire.

      - Coupling ring: Stainless Steel 1.4571 (equivalent to 316Ti)

Note to specifier:  specify Titanium, grade 2 for use in seawater or aquaculture.

      - Ring: POM

      - Screw: Stainless Steel V4A

Note to specifier:  specify Polyamide 6.6 for use in seawater or aquaculture.

      - O-ring:  NBR

      - Enclosure:  POM

      - Nut:  Stainless Steel 1.4571 (equivalent to 316Ti)

      - Protection ring:  POM

Note to specifier:  specify Titanium, grade 2 for use in seawater or aquaculture.

      - Cable sheath:  PUR

      - Protective cap:  PVC

Note to specifier:  specify POM threaded plug for use in seawater or aquaculture.

      - Protection rating:  IP68 (waterproof)

      - Warranty:  12 months

  - ACCESSORIES

Note to specifier:  Specify sensor mounting assembly and other accessories as required.

    - Handrail sensor mounting assemblies:

      - YSI model 2458000Y SMK Quick Release Stainless Steel Handrail Mounting Bracket with 1.5-inch Mounting Adapter

Note to specifier:  A handrail mount is the most appropriate option for most installations.  Many other standard mounting options are available.  Consult YSI for more information.  Requires 1.5-in. PVC pipe cut to desired length not included with mounting assembly from YSI.

    - Compressed air cleaning system [Options: external air supply; cleaning air box supply]

Note to specifier:  Cleaning air box option shown.  External air supply option requires a source of air at 45 to 105 psig.  See notes in text boxes for details of external air supply option.

      - Model:  Cleaning Air Box

Note to specifier:  For external air supply option specify valve module MIQ/CHV PLUS for use with a 2020 XT controller or valve module DIQ/CHV for use with a 182 controller.

      - The cleaning system shall use clean, dry, oil free air.

      - Cleaning intervals and duration cycles: user-programmable.

      - Cleaning head Model CH:  three equally-spaced air exit nozzles.

      - Cleaning pressure: between 30 and 50 psi.

      - Each sensor shall have a dedicated cleaning compressor.

Note to specifier:  Not a requirement for external air supply option.

      - The cleaning system shall use a braided hose with quick disconnects between the compressor and sensor cleaning head.

      - Power supply:  115 VAC.

Note to specifier:  Specify 230 VAC if required.  Not a requirement for external air supply option.

- EXECUTION

  - INSTALLATION

    - Immersion sensors:

      - Immerse sensor face a minimum of 2 in. (50 mm) and a maximum of 80 in. (2 m) below the surface.

      - Protect the probe against the oncoming flow of large objects.

    - Sensor connection cable

      - Bend radius

        - Permanent bend:  not less than 3.2 in. (80 mm).

        - One-time bend:  not less than 2 in. (50 mm).

  - START-UP

    - Install ammonium sensors in strict accordance with the manufacturer’s instructions and recommendations.

    - Manufacturer’s representative will include a half-day of start-up service by a factory-trained technician, if requested.

      - Contractor will schedule a date and time for start-up.

      - Contractor will require representatives of the following be present during the start-up:

        - General contractor

        - Electrical contractor

        - YSI factory-trained representative

        - Owner’s personnel

        - Engineer

- END OF SECTION