- GENERAL

  - DESCRIPTION

    - Section Includes

      - Sensors, cables, and associated equipment for measuring the sludge blanket profile in wastewater treatment settling tanks and gravity sludge thickeners.  Controllers and modules required for a complete monitoring system are specified elsewhere.

    - Scope

      - Furnish, install, calibrate, test, adjust, and place into satisfactory operation sludge interface level measurement system as shown on the Drawings and specified herein.

      - The Drawings and Specifications illustrate and specify functional and general construction requirements of sludge interface level sensors and do not necessarily show or specify all components, wiring, piping, and accessories required to make a completely integrated system. Provide all components, piping, wiring, accessories, and labor required for a complete and integrated system.

    - Coordination:  Coordinate with other suppliers for installation of all items specified herein and required to ensure the complete and proper interfacing of all the components and systems.

  - PERFORMANCE REQUIREMENTS

    - Design Requirements

      - Design sludge interface level measurement system for continuous monitoring in situ.

      - Sludge blanket profile measurement system shall be a component of a process monitoring system capable of monitoring up to 20 parameters simultaneously on each controller.  Measurement locations shall be networked together in a linear, star, or branched topology with a single 2-wire cable that distributes 12 V power and communications.

Note to specifier:  Item 1.2.A.2 is for a System 2020XT monitoring system.

      - The sludge blanket profile sensor assembly shall be a separate unit from the sensor connection cable and able to be located anywhere in the monitoring network a sensor connection terminal is available.

    - Performance Requirements

      - Operating range

        - Temperature:  31°F to 122°F (0°C to 50°C)

        - Pressure range:  < 0.3 bar

        - pH:  4 S.U. to 12 S.U.

        - Flow velocity:  10 ft./sec.

        - Immersion depth:  2 in. to 10 ft.

      - Measuring range: 1.32 ft. to 49.2 ft.

      - Measuring Accuracy:  4 in.

      - Resolution: 0.4 in.

  - QUALITY ASSURANCE

    - Acceptable Manufacturers:

      - Furnish sludge interface level measurement system by the named manufacturers.

      - The named manufacturers have been specified to establish the standard of quality and performance of the equipment to be supplied.

      - Manufacturer shall be ISO 9001 certified.

  - PRODUCT DELIVERY, STORAGE, AND HANDLING

    - Sludge blanket profile measurement system shall not be delivered to the site until all product information and system shop drawings for the system have been approved.

    - Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

    - Storage and Handling Requirements:

      - Store and handle materials in accordance with manufacturer’s instructions.

      - Keep materials in manufacturer’s original, unopened containers and packaging until installation.

      - Store materials in clean, dry area indoors.

      - Protect materials during storage, handling, and installation to prevent damage.

      - Temperature range for storage:  23°F to 122°F (-5°C to 50°C)

  - SUBMITTALS

    - Product data

      - Sensor operating manual.

      - Mounting bracket / sensor holder installation instructions.

    - Manufacturer’s Certifications:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

    - Warranty documentation:  Submit manufacturer’s standard warranties.

- PRODUCTS

  - GENERAL

    - Measurement principle shall be acoustic by measuring the elapsed time of acoustic echoes from a submersible ultrasonic transducer to interfaces between layers of varying density.

    - Connect sludge interface level sensor to field-mounted junction box or expansion modules specified in Section 40 95 00 with sensor connecting cable as specified in Section 2.3.A.2.

    - Sludge interface level measuring system components shall be designed to be part of a process control system with enhanced protection from overvoltage due to lightning and power supply fluctuations according to EN 61326 when installed using manufacturer’s recommended components per manufacturer’s instructions.

  - MANUFACTURER

    - Provide products from the following manufacturer:

      - YSI, Incorporated, 1700/1725 Brannum Lane, Yellow Springs, OH  45387.  1-800-765-4974.

  - MANUFACTURED UNIT

    - The Sludge interface level measurement system consists of the following:

      - Model IFL 701 IQ Sludge Interface Level Sensor [Model IFL 700 IQ Sludge Interface Level Sensor].

        - The sensor shall be factory-calibrated and ready for measurement out of the box with input of sensor immersion depth and settling tank depth.

        - The sensor shall include intelligent signal processing to filter out undesirable signals.

        - In combination with the 2020XT controller, the sensor shall generate a graphical representation of the water column.

        - The sensor shall include self-diagnostics to detect moisture contamination in the sensing element.

        - The sensor shall have a digital output signal.

        - The sensor shall detach from sensor cable allowing for easy replacement or repair.

        - The sensor shall include a maintenance-free and wear-free mechanical non-contacting wiper. Models with replaceable wiper blades and o-rings shall not be accepted.

Note to specifier:  Model IFL 700 IQ includes a non-contact wiper for displacing air bubbles and algae accumulation.  Select IFL 700 IQ and include Item 2.3.A.h for measurements in settling tanks where rotating surface skimmers are not present.

      - SACIQ-x,x [SACIQ-x,x SW] sensor connection cable.

        - Capable of transmitting digital communications and low voltage (24V) power

        - Integrated shield.

        - Connections

          - Sensor-side:  Quick fastener (threaded)

          - Controller-side:  tinned conductors

Note to specifier:  Specify appropriate length of cable in meters, e.g. SACIQ-1,5 is 1.5 m.  Standard lengths are 1.5 m, 7m, and 15m.  Custom lengths up to 100 m are available.  Select SACIQ-x,x for measurements in water/wastewater applications.  Select SACIQ-x,x SW for measurements in seawater/aquaculture and other highly corrosive environments.

  - MATERIALS

    - Sensor

      - Body:  V4A Stainless Steel 1.4571 (equivalent to 316Ti)

      - Plug head and transition unit:  POM

      - Ultrasound unit:  PVC-C

      - Safety

        - Certification: CE,  cETL, ETL

      - Warranty: 2 years

    - Sensor connection cable

      - Conductors:  Tin-coated stranded copper wire.

      - Coupling ring: Stainless Steel 1.4571 (equivalent to 316Ti)

      - Ring: POM

      - Screw: Stainless Steel V4A

      - O-ring:  NBR

      - Enclosure:  POM

      - Nut:  Stainless Steel 1.4571 (equivalent to 316Ti)

      - Protection ring:  POM

      - Cable sheath:  PUR

      - Protective cap: PVC

      - Protection rating:  IP68 (waterproof)

      - Warranty:  12 months

  - ACCESSORIES

Note to specifier:  Specify sensor mounting assembly and other accessories as required.

    - Handrail Sensor mounting assemblies:

      - YSI model 481208Y IFL-PM handrail mounting bracket

      - YSI model 481206Y IFL-E deflector plate

Note to specifier:  Requires 1.25-in. metal pipe cut to desired length not included with mounting assembly from YSI.

- EXECUTION

  - INSTALLATION

    - Immersion sensors:

      - Immerse sensor to provide a minimum distance of 2 in. (5 cm) between the bottom face of the sensor and the water surface.

      - Immerse sensor to provide a minimum distance of 16 in. (40 cm) between the bottom face of the sensor and the top of the sludge layer.

      - Install the sensor in a vertical orientation with the transducer on the bottom.

      - Install sensor a minimum distance from tank walls and other obstructions in accordance with manufacturer’s instructions.

    - Sensor connection cable

      - Bend radius

        - Permanent bend:  not less than 3.2 in. (80 mm).

        - One-time bend:  not less than 2 in. (50 mm).

  - START-UP

    - Install sludge interface level sensors in strict accordance with the manufacturer’s instructions and recommendations.

    - Manufacturer’s representative will include a half-day of start-up service by a factory-trained technician, if requested.

      - Contractor will schedule a date and time for start-up.

      - Contractor will require representatives of the following be present during the start-up:

        - General contractor

        - Electrical contractor

        - YSI factory-trained representative

        - Owner’s personnel

        - Engineer

- END OF SECTION