- GENERAL

  - SUMMARY

    - Section Includes

      - Sensors, cables, and associated equipment for optical measurement of UV transmittance and absorption in water and wastewater treatment systems.  Controllers and modules required for a complete monitoring system are specified elsewhere.

    - Scope

      - Furnish, install, calibrate, test, adjust, and place into satisfactory operation UV transmittance measurement systems as shown on the Drawings and specified herein in accordance with the contract documents.

      - The Drawings and Specifications illustrate and specify functional and general construction requirements of UV transmittance measurement systems and do not necessarily show or specify all components, wiring, piping, and accessories required to make a completely integrated system. Provide all components, piping, wiring, accessories, and labor required for a complete workable and integrated system.

    - Coordination:  Coordinate with other suppliers for installation of all items specified herein and required to ensure the complete and proper interfacing of all the components and systems.

  - PERFORMANCE REQUIREMENTS

    - Design Requirements

      - Design UV transmittance measurement system for continuous monitoring in situ.

      - UV transmittance measurement system shall be a component of a process monitoring system capable of monitoring up to 20 parameters simultaneously on each controller.  Measurement locations shall be networked together in a linear, star, or branched topology with a single 2-wire cable that distributes 12 V power and communications.

      - The UV transmittance sensor assembly shall be a separate unit from the sensor connection cable and able to be located anywhere in the monitoring network a SensorNet terminal is available.

    - Performance Requirements

      - Operating range

        - Temperature:  32°F to 113°F (0°C to 45°C)

        - Pressure:  less than or equal to 1 bar

        - pH:  4 S.U. to 12 S.U.

        - Flow velocity:  < 3 m/s

    - Measuring range [IQ UVT-254 701]

      - UVT-254

        - 0.0 to 100.0%

      - SAC-254

        - 0 to 3,000 / m (soluble)

        - 0 to 3,000 / m (total)

      - COD (correlated)

        - 0 to 12,500 mg/L (soluble)

        - 0 to 20,000 mg/L (total)

      - BOD (correlated)

        - 0.0 to 8,000 mg/L

      - TOC (correlated)

        - 0.0 to 20,000 mg/L

      - DOC (correlated)

        - 0.0 to 12,500 mg/L

    - Measuring range [IQ UVT-254 705]

      - UVT-254

        - 0.0 to 100.0%

      - SAC-254

        - 0 to 600 / m (soluble)

        - 0 to 600 / m (total)

      - COD (correlated)

        - 0 to 800 mg/L (soluble)

        - 0 to 800 mg/L (total)

      - BOD (correlated)

        - 0.0 to 500 mg/L

      - TOC (correlated)

        - 0.0 to 500 mg/L

      - DOC (correlated)

        - 0.0 to 500 mg/L

    - Resolution [IQ UVT-254 701]

      - UVT-254

        - 0.1%

      - SAC-254

        - 1 / m (soluble)

        - 1 / m (total)

      - COD (correlated)

        - 1 mg/L (soluble)

        - 1 mg/L (total)

      - BOD (correlated)

        - 1 mg/L

      - TOC (correlated)

        - 1 mg/L

      - DOC (correlated)

        - 1 mg/L

    - Resolution [IQ UVT-254 705]

      - UVT-254

        - 0.1%

      - SAC-254

        - 0.1 / m (soluble)

        - 0.1 / m (total)

      - COD (correlated)

        - 0.1 mg/L (soluble)

        - 0.1 mg/L (total)

      - BOD (correlated)

        - 0.1 mg/L

      - TOC (correlated)

        - 0.1 mg/L

      - DOC (correlated)

        - 0.1 mg/L

    - Signal averaging:  user selectable to provide a t90 from 10 min. to 60 min.

  - QUALITY ASSURANCE

    - Acceptable Manufacturers:

      - Furnish UV transmittance measurement system by the named manufacturers.

      - The named manufacturers have been specified to establish the standard of quality and performance of the equipment to be supplied.

      - Manufacturer shall be ISO 9001 certified.

  - PRODUCT DELIVERY, STORAGE, AND HANDLING

    - Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

    - Storage and Handling Requirements:

      - Store and handle materials in accordance with manufacturer’s instructions.

      - Keep materials in manufacturer’s original, unopened containers and packaging until installation.

      - Store materials in clean, dry area indoors.

      - Protect materials during storage, handling, and installation to prevent damage.

      - Temperature range for storage:  15°F to 120°F (-10°C to 50°C)

  - SUBMITTALS

    - Product data

      - Sensor operating manual.

      - Mounting bracket / sensor holder installation instructions.

    - Manufacturer’s Certifications:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

    - Warranty documentation:  Submit manufacturer’s standard warranties.

- PRODUCTS

  - GENERAL

    - Measurement principle shall be optical based on measurement of the transmission of light through sample from a light source that emits light at a wavelength of 254 nm in the ultraviolet range and a wavelength of 550 nm in the visible range.

    - Connect UV transmittance sensors to field-mounted expansion modules specified in Section 40 95 00 with appropriate sensor connecting cable.

    - UV transmittance measuring system components shall be designed to be part of a process control system with enhanced protection against overvoltage due to lightning and power supply fluctuations according to EN61326 when installed using manufacturer’s recommended components per manufacturer’s instructions.

  - MANUFACTURER

    - Provide products from the following manufacturer:

      - YSI Incorporated, 1700/1725 Brannum Lane, Yellow Springs, OH  45387.  1-800-765-4974.

  - MANUFACTURED UNIT

    - The UV transmittance measurement system consists of the following:

      - Model IQ UVT-254 UV 701 / IQ UVT-254 705 UV transmittance sensor.

        - The sensor shall have a non-mechanical integrated ultrasonic cleaning system.

        - The sensor shall have a digital output signal.

        - The sensor shall detach from sensor cable allowing for easy replacement or repair.

Note to specifier:  Select appropriate model (701 with a 1 mm measuring gap for untreated and relatively polluted wastewater; 705 with a 5 mm measuring gap for treated and relatively clean wastewater).

      - SACIQ-x,x [SACIQ-x,x SW] sensor connection cable.

        - Capable of transmitting digital communications and low voltage (24V) power

        - Integrated shield.

        - Connections

          - Sensor-side:  Quick fastener (threaded)

          - Controller-side:  tinned conductors

Note to specifier:  Specify appropriate length of cable in meters, e.g. SACIQ-1,5 is 1.5 m.   Standard lengths are 1.5 m, 7m, and 15m.  Custom lengths up to 100 m are available.  Select SACIQ-x,x for measurements in water/wastewater applications.  Select SACIQ-x,x SW for measurements in seawater/aquaculture and other highly corrosive environments.

  - MATERIALS

    - Sensor

      - Shaft:  Titanium Grade 2

      - Measurement window:  sapphire

      - Center piece, end cap:  PEEK

      - Plug head connector housing:  POM

      - Plug:  ETFE

      - Protective ring:  POM

      - EMI/RFI conformance

        - EN 61326 Class B

        - FCC Class A

      - Safety

        - Certification: CE,  cETLus

      - Protection rating:  IP68

      - Warranty: 2 yrs.

    - Sensor connection cable

      - Conductors:  Tin-coated stranded copper wire

      - Coupling ring: Stainless Steel 1.4571 (equivalent to 316Ti)

      - Ring: POM

      - Screw: Stainless Steel V4A

      - O-ring:  NBR

      - Enclosure:  POM

      - Nut:  Stainless Steel 1.4571 (equivalent to 316Ti)

      - Protection ring:  POM

      - Cable sheath:  PUR

      - Protective cap: PVC

      - Protection rating:  IP68 (waterproof)

      - Warranty:  12 months

  - ACCESSORIES

Note to specifier:  Specify sensor mounting assembly and other accessories as required.

    - Handrail swing mounting assembly

      - YSI model 109 281Y Pipe Mounting Stand

      - YSI model 109 272Y Swing Mounting Assembly

      - YSI model 481 073Y Horizontal Chain Mount [horizontal mount option]

      - YSI model 109 320Y Single Sensor Holder

    - Handrail Pipe mounting assembly:

      - YSI model 2458000Y SMK Quick Release Stainless Steel Handrail Mounting Bracket with 1.5-inch Mounting Adapter

Note to specifier:  A handrail mount is the most appropriate option for most installations.  Many other standard mounting options are available.  Consult YSI for more information.

    - Compressed air cleaning system [Options: external air supply; cleaning air box supply]

Note to specifier:  Cleaning air box option described.   See notes in text boxes for details of external air supply option.

      - Model:  Cleaning Air Box

Note to specifier:  For external air supply option specify valve module MIQ/CHV PLUS for use with 2020 XT controller or valve module DIQ/CHV for use with 182 controller.

      - The cleaning system shall use clean, dry, oil-free air.

      - Sensor-controlled cleaning cycles.

      - Cleaning set Model SET/AP:  connector and 15 m of tubing.

      - Cleaning pressure: 30 to 50 psi.

      - Each sensor shall have a dedicated cleaning compressor.

Note to specifier:  Not a requirement for external air supply option.

      - Power supply:  115 VAC.

Note to specifier:  Specify 230 VAC if required.  Not a requirement for external air supply option.

- EXECUTION

  - INSTALLATION

    - Immersion sensors:

      - Immerse sensor to a depth sufficient to fill the measuring gap.

      - Protect the probe against the oncoming flow of large objects.

      - Install instrument to prevent air bubbles from gathering on the optical sensing element.

        - Horizontal installation:  Align sensor parallel to flow with measuring gap opening on the side

        - Vertical installation:  Align measuring gap perpendicular to the flow direction.

      - Impact protection

        - Mount shock protectors to absorb inadvertent impacts.

        - Mount sensor so that it cannot knock against a wall or other obstacle.

    - Sensor connection cable

      - Bend radius

        - Permanent bend:  not less than 3.2 in. (80 mm).

        - One-time bend:  not less than 2 in. (50 mm).

  - START-UP

    - Contractor will install UV transmittance measurement system in strict accordance with the manufacturer’s instructions and recommendations.

    - Manufacturer’s representative will include a half-day of start-up service by a factory-trained technician, if requested.

      - Contractor will schedule a date and time for start-up.

      - Contractor will require representatives of the following be present during the start-up:

        - General contractor

        - Electrical contractor

        - YSI factory-trained representative

        - Owner’s personnel

        - Engineer

- END OF SECTION